## ALF series Miniature Circuit breaker(MCB)

>> Introduction

ALF  are intended for protecting distribution and group systems having different loads:
- electric appliances, lighting – V characteristic switches;
- drives with moderate starting currents (compressor, fan group) - C characteristic switches;
- drives with high starting currents (hoisting mechanisms, pumps) - D characteristic switches;
Miniature circuit breaker ALF are recommended for use in electrical distribution panels of residential and public buildings.

>> Advantages

·         Two types of short circuit protection.

·         Wide range of operating temperatures from –40 to +50° С.

·         Updated wider engagement lever with improved contact area.

·         Notches on terminal clamps provide for lowering thermal losses and boosting the mechanical stability of connection.

| MCB ALF |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| For protection of general power distribution (IEC/EN 60898-1) |  |  |  |  |  |  |
| Poles |  |  | 1P | 2P | 3P | 4P |
| Electrical performance |  |  |  |  |  |  |
| Functions |  |  | short circuit protection,overload protection,isolationg,control |  |  |  |
| Rated frequency f Hz |  |  | 50-60Hz |  |  |  |
| Rated working voltage Ue V AC |  |  | 230/400 | 400 |  |  |
| Rated current In A |  |  | 6,10,16,20,25,32,40,50,63 |  |  |  |
| Rated insulated voltage Ui V |  |  | 500 |  |  |  |
| Impulse withstand voltage Uimp kV |  |  | 4 |  |  |  |
| Instantaneous tripping type | ALF |  | B/C/D |  |  |  |
| Rated short circuit Icn(kA) | ALF |  | 4.5 |  |  |  |
| Release type |  |  | Thermal magnetic type |  |  |  |
| Service life(O~C) | Mechanical | Actual value | 20000 |  |  |  |
|  |  | Standard value | 4000 |  |  |  |
|  | Electrical | Actual value | 8000 |  |  |  |
|  |  | Standard value | 4000 |  |  |  |
| Connection and installation |  |  |  |  |  |  |
| Protectiom degree |  |  | IP20 |  |  |  |
| Wire mm² |  |  | 1~35 |  |  |  |
| Working temperature |  |  | -5 ～+40℃ |  |  |  |
| Resistance to humidity and heat |  |  | Class 2 |  |  |  |
| Altitude above sea |  |  | ≤2000 |  |  |  |
| Relative humidity |  |  | +20℃ , ≤90% ;+40℃ , ≤50% |  |  |  |
| Pollution degree |  |  | 2 |  |  |  |
| Installation environment |  |  | Avoid obvious shock and vibration |  |  |  |
| Installation class |  |  | Class Ⅱ , Class Ⅲ |  |  |  |
| Mounting |  |  | DIN35 rail |  |  |  |
| Combination with accessories |  |  |  |  |  |  |
| Auxiliary contact |  |  | Yes |  |  |  |
| Alarm contact |  |  | Yes |  |  |  |
| Shunt release |  |  | Yes |  |  |  |
| Undervoltage release |  |  | Yes |  |  |  |
| Auxiliary contact+Alarm contact |  |  | Yes |  |  |  |
| Dimensions(mm) (WxHxL) |  | a | 17.5 | 35 | 52.5 | 70 |
|  |  | b | 80.2 | 80.2 | 80.2 | 80.2 |
|  |  | c | 76.5 | 76.5 | 76.5 | 76.5 |