DAB6-125 Miniature circuit Breaker

>>  Application

DAB6-125 is such features as delicate appearance, light weight, excellent and reliableperformance, high breaking capacity, rapid tripping and mounted by rail. Its enclosure and com-ponents adopts high fire-retarding and shock-resistance plastic of long durability. It mainly servesfor protecting the circuits of AC 50Hz, 230V of single pole, 400V of two poles or three or fourpoles from overload or short-circuit, and also for unfrequent making and breaking electricalapparatus and lighting circuit.It conforms with the standards of IEC60947-2.

|  | >> Technical Features |
| --- | --- |

| MCB DAB6-125 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| For protection of general power distribution (IEC/EN 60898-1) |  |  |  |  |  |  |  |
| Poles |  |  |  | 1P | 2P | 3P | 4P |
| Electrical performance |  |  |  |  |  |  |  |
| Functions |  |  |  | short circuit protection,overload protection,isolationg,control |  |  |  |
| Rated frequency f(Hz) |  |  |  | 50-60Hz |  |  |  |
| Rated working voltage Ue(V) AC |  |  |  | 230/400 | 400 |  |  |
| Rated current In(A) |  |  |  | 63,80,100,125 |  |  |  |
| Rated insulated voltage Ui (V) |  |  |  | 500 |  |  |  |
| Impulse withstand voltage Uimp( kV) |  |  |  | 4 |  |  |  |
| Instantaneous tripping type |  | DAB6-125N |  | B/C/D |  |  |  |
|  |  | DAB6-125H |  | B/C/D |  |  |  |
| Rated short circuit Icn(kA) |  | DAB6-125N |  | 6 |  |  |  |
|  |  | DAB6-125H |  | 10 |  |  |  |
| Release type |  |  |  | Thermal magnetic type |  |  |  |
| Service life(O~C) | Mechanical |  | Actual value | 8500 |  |  |  |
|  |  |  | Standard value | 4000 |  |  |  |
|  | Electrical |  | Actual value | 1500 |  |  |  |
|  |  |  | Standard value | 1000 |  |  |  |
| Connection and installation |  |  |  |  |  |  |  |
| Protectiom degree |  |  |  | IP20 |  |  |  |
| Wire(mm²) |  |  |  | 1~35 |  |  |  |
| Working temperature |  |  |  | -5～+40℃ |  |  |  |
| Resistance to humidity and heat |  |  |  | Class 2 |  |  |  |
| Altitude above sea |  |  |  | ≤2000 |  |  |  |
| Relative humidity |  |  |  | +20℃ ,≤90% ;+40℃ ,≤50% |  |  |  |
| Pollution degree |  |  |  | 2 |  |  |  |
| Installation environment |  |  |  | Avoid obvious shock and vibration |  |  |  |
| Installation class |  |  |  | ClassⅡ , ClassⅢ |  |  |  |
| Mounting |  |  |  | DIN35 rail |  |  |  |
| Dimensions(mm) (WxHxL) |  |  | a | 27 | 54 | 81 | 108 |
|  |  |  | b | 80 | 80 | 80 | 80 |
|  |  |  | c | 73 | 73 | 73 | 73 |

>>  The over-current protection property

| Ambient Temperature | Initial Status | Test Current | Expected Result | Expected Result | NOte |
| --- | --- | --- | --- | --- | --- |
| 40±2oC | Cold position | 1.05In(In≤63A) | t≤1h | Non-release | - |
|  | Cold position | 1.05In (In[63A) | t≤2h | Non-release | - |
|  | Carried out immedi-ately after previous test | 1.30In(In≤63A) | t < 1h | Release | Current smoothlyrises to specified value within 5s |
|  |  | 1.30In (In>63A) | t < 2h | Release |  |
| -5~+40oC | Cold position | 8.00In | t≤0.2s | Non-release | - |
|  | Cold position | 12.00In | t< 0.2s | Non-release | - |

>> Applicable conducting wire

| Rated current(A) | Nominal cross section of wire mm2 |
| --- | --- |
| 63A | 16 |
| 80A | 25 |
| 100A | 35 |

>>  Dimension

>> Advantages

·  Two types of overload and short circuit protection.

·  Independent contact position indicator.

·  DIN rail latch with a double fixed position.

·  Wide range of operating temperatures from –40 to +50° С.

·  Updated wider engagement lever with improved contact area.

·  Notches on terminal clamps provide for lowering thermal losses and boosting the mechanical stability of connection.

·  Higher switching capacity of 10 kA provides for installing DAB6-125 as incoming circuit breakers.